## Sheet1
Diaphram Meter | u16 |  |  | 0.025 | 0.03
Rotary Meter | No Meter |  |  | 0 | 0
|  | Volume Per Meter | Length (m) | Installation Volume (m3) | Purge Volume (m3)
Pipesize 1 | DN15 | 0.00024 | 1 | 0.00024 | 0.00036
Pipesize 2 | DN20 | 0.00046 | 1 | 0.00046 | 0.00069
Pipesize 3 | DN32 | 0.0011 | 15 | 0.0165 | 0.02475
Pipesize 4 | DN100 | 0.009 | 10 | 0.09 | 0.135
Pipesize 5 | DN200 | 0.035 | 0 | 0 | 0
Pipesize 6 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 7 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 8 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 9 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 10 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 11 | DN15 | 0.00024 | 0 | 0 | 0
Pipesize 12 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 13 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 14 | DN50 | 0.0024 | 0 | 0 | 0
Pipesize 15 | DN50 | 0.0024 | 0 | 0 | 0
Purge hose | 20mm | 0.00046 | 10 |  | 0.0069
Fittings Volume 10% |  |  |  | 0.01072 | 0.02412
Total Volume |  |  |  | 0.14292 | 0.22182
Maximum Purge flow Rate Qp (m3/hr)
Pipe Diameter to be purged | DN100 | 20 |  | Purge Time (secs) | 39.9276
| Type | Range | GRM | TTD max
Gauge choice | Elec 2 dp | 0-200 | 0.1 | 15
| Gas Type | Test using Gas | Test Using N2
Fuel type | NATURAL | 42 | 67
| TTD using Gas (mins) |  | TTD Using N2 (mins) |  | Inadequately ventilated areas (Area type A)
TTD New/Existing type A | 0.60026 |  | 0.95756 |  | Adequately ventilated internal areas of volume less than 60 m3 (Area Type B)
Existing Type C &D | 0.028212 |  | 0.045006 |  | Adequately ventilated internal areas of volume 60 m3 or greater and
Existing In Type A | 0.028012 |  | 0.044686 |  | external exposed areas (Area type C)
Room Voulme | 60 |  |  |  | Underground (buried) (Area type D).
| Type | F3 Using Gas | F3 Using N2
Fuel Type | Butane | 0.059 | 0.134
TTD From above | 2.64
Gauge Movement | 3
| MPLR Gas | MPLR N2
MPLR | 0.0095821 | 0.021763 |  |  | See Table 7 and 8 for MPLR

## Data
Table 3 |  |  | Table 4 |  |  | Purge Hose Vol |  | Table 12
U6 | 0.008 | 0.002 | DN15 | 0.00024 |  | 20mm | 0.00046 | DN20 | 0.6 | 0.01 | 0.7 | Table 10 F1
u16 | 0.025 | 0.006 | DN20 | 0.00046 |  | 25mm | 0.00064 | DN25 | 0.6 | 0.02 | 1 | Gas Type | Gas | Nitorgen
U25 | 0.037 | 0.01 | DN25 | 0.00064 |  | 32mm | 0.0011 | DN32 | 0.6 | 0.03 | 1.7 | NATURAL | 42 | 67
U40 | 0.067 | 0.02 | DN32 | 0.0011 |  | 40mm | 0.0015 | DN40 | 0.6 | 0.05 | 2.5 | PROPANE | 102 | 221
U65 | 0.1 | 0.025 | DN40 | 0.0015 |  | 50mm | 0.0024 | DN50 | 0.6 | 0.08 | 4.5 | BUTANE | 128 | 305
U100 | 0.182 | 0.057 | DN50 | 0.0024 |  | 65mm | 0.0038 | DN80 | 0.6 | 0.19 | 11 | LPG/AIR (SNG) | 45 | 60
U160 | 0.304 | 0.071 | DN65 | 0.0038 |  | 80mm | 0.0054 | DN100 | 0.6 | 0.33 | 20 | LPG/AIR (SMG) | 28 | 33
No Meter | 0 | 0 | DN80 | 0.0054 |  | 100mm | 0.009 | DN125 | 0.6 | 0.5 | 30 | COAL GAS | 20 | 31
|  |  | DN100 | 0.009 |  | 125mm | 0.014 | DN150 | 0.6 | 0.7 | 38
|  |  | DN125 | 0.014 |  | 150mm | 0.02 | DN200 | 0.7 | 1.32 | 79
|  |  | DN150 | 0.02 |  | 200mm | 0.035 | DN250 | 0.8 | 2.35 | 141
|  |  | DN200 | 0.035 |  |  |  | DN300 | 0.9 | 3.6 | 216 | Table 11 F3
|  |  | DN250 | 0.053 |  |  |  | DN400 | 1 | 7.9 | 473 | operating fuel | F3 Gas | F3 N2
|  |  | DN300 | 0.074 |  |  |  | DN450 | 1 | 9.6 | 575 | Natural | 0.059 | 0.094
|  |  | DN350 | 0.089 |  |  |  | DN600 | 1.2 | 21 | 1230 | Propane | 0.059 | 0.126
|  |  | DN400 | 0.118 |  |  |  | DN750 | 1.5 | 40 | 2390 | Butane | 0.059 | 0.134
|  |  | DN450 | 0.151 |  |  |  | DN900 | 1.5 | 57 | 3440 | LPG/air (SNG) | 0.059 | 0.078
|  |  | 15mm Cu | 0.00014 |  |  |  | DN1200 | 1.7 | 116 | 6960 | LPG/Air (SMG) | 0.059 | 0.069
|  |  | 22mm Cu | 0.00032 | [7 empty] | Coal Gas | 0.059 | 0.09
|  |  | 28mm Cu | 0.00054
|  |  | 35mm Cu | 0.00084
|  |  | 42mm Cu | 0.0012
|  |  | 54mm Cu | 0.0021
|  |  | 67mm CU | 0.0033
Table 3 RD |  |  | Table 6
No Meter | 0 |  | Gauge | Range | GRM | TTD Max
DN32 | 0.0011 |  | Water SG | 0-120 | 0.5 | 30
DN40 | 0.0015 |  | High SG | 0-200 | 1 | 45
DN50 | 0.0024 |  | Elec 1 dp | 0-200 | 0.5 | 30
DN65 | 0.0038 |  | Elec 2 dp | 0-200 | 0.1 | 15
DN80 | 0.0054 |  | Elec 1dp | 0-2000 | 0.5 | 30
DN100 | 0.009 |  | Elec 0dp | 0-20000 | 5 | 60
DN125 | 0.014 |  | Mercury | 0-1000 | 7 | 60
DN150 | 0.02
DN200 | 0.035
DN250 | 0.053
DN300 | 0.074
DN350 | 0.089
DN400 | 0.118
DN450 | 0.151